## Table details
SLD Required informations
A |  |  |  |  | B |  |  | C | D | E | F | G | H |  |  |  |  | refer to B | I | J | K
Main Breaker Rating Amperage(A): can be MCCB or MCB | Type of MCB A/B/C/D | Single Phase/ SPN | Three Phase/ TPN | Breaking Current (kA) 6/10/25/35/50 | Type of incoming cable: PVC PVC/PVC XLPE Armoured | Cable Size mm2 | how many Core of Cable 1C/2C/4C | Required Bi Connector Y/N | Required indicator lights. Y/N 3 phase | Indicator lights Fuse 2A. Y/N Required Voltmeter | Required ELR set up Y/N *ELR Set required LEW inputs | RCCB Required before sub breakers Y/N required LEW inputs | Sub Breaker. Means outgoing breakers: outgoing MCB | Type of MCB A/B/C/D | Single Phase/ SPN | Three Phase/ TPN | Breaking Current (kA) 6/10/25/35/50 | Cable size refer to Column B | Circuit label. Single phase starts with P1 3 Phase starts with L1P1 I need to provide some example on this | Outgoing circuit. please indicate quantity able to indicate its designation | Outgoing Isolator. Please indicate quantity able to indicate its designation
32 | usually Type B or C | usually SPN |  |  |  | 6 + 6mmsq E | [6 empty] | 6
40 | [5 empty] | 10 + 10mmsq E | [6 empty] | 10
63 | [5 empty] | 16 + 16mmsq E | [6 empty] | 16
80 | [5 empty] | 25 + 16mmsq E | [6 empty] | 20
100 | [5 empty] | 35 + 16mmsq E | [6 empty] | 32
150 | [5 empty] | 70 | [6 empty] | 63
200 | [5 empty] | 95 | [6 empty] | 80
250 | [5 empty] | 95 | [6 empty] | 100
300 | [5 empty] | 120 | [6 empty] | 150
400 | [5 empty] | 185 | [6 empty] | 200
630 | [5 empty] | 300 | [6 empty] | 250
800 | [5 empty] | 500 | [6 empty] | 300
1000 | ACB- Air Circuit Breaker |  |  |  |  | 500 | [6 empty] | 400
1200 | ACB- Air Circuit Breaker |  |  |  |  | 630 | [6 empty] | 630
1600 | ACB- Air Circuit Breaker |  |  |  |  | 630 | [6 empty] | 800
1000
1200
1600

## Table form
INCOMING
CABLE |  |  | MAIN BREAKER |  |  |  |  | MAIN EARTH PROTECTION
MINIMUM SIZE OF PHASE, NEUTRAL, EARTH | QUANTITY & NO. OF CORE | TYPE | RATING | NO. OF POLE (SPN/DP/TPN/4P) | TYPE (MCB/MCCB/ACB) | QUANTITY | KA RATING | TYPE (RCCB/ELR/EFR) | RATING | NO. OF POLE (DP/4P) | QUANTITY | SENSITIVITY/SETTING
6 + 6mmsq E | 4 X 1 CORE | PVC | 32 |  |  |  |  | RCCB | 40A | 4P |  | 30mA
10 + 10mmsq E |  | PVC/PVC | 40 |  |  |  |  | ELR |  |  |  | 2A, 0.3 SEC
16 + 16mmsq E |  | XLPE/PVC | 63 | DP | MCB |  | 10 | EFR |  |  |  | 50A, 0.3 SEC
25 + 16mmsq E | 1 X 4 CORE |  | 80
35 + 16mmsq E |  |  | 100
70 |  |  | 150
95 |  |  | 200 | TPN | MCCB |  | 35
95 |  |  | 250
120 |  |  | 300
185 |  |  | 400
300 |  |  | 630
500 |  |  | 800
500 |  |  | 1000
630 |  |  | 1200
630 |  |  | 1600 | 4P | ACB |  | 50
OUTGOING
CABLE |  |  | SUBMAINS BREAKER |  |  |  |  | EARTH PROTECTION
MINIMUM SIZE OF PHASE, NEUTRAL, EARTH | QUANTITY & NO. OF CORE | TYPE | RATING | NO. OF POLE (SPN/DP/TPN/4P) | TYPE (MCB/MCCB/ACB) | QUANTITY | KA RATING | TYPE (RCCB/ELR/EFR) | RATING | NO. OF POLE (DP/4P) | QUANTITY | SENSITIVITY/SETTING
1.5 |  |  | 6
1.5 |  |  | 10
2.5 |  |  | 16
2.5 |  |  | 20
6 |  |  | 32
16 |  |  | 63
35 |  |  | 80
35 |  |  | 100
70 |  |  | 150
95 |  |  | 200
95 |  |  | 250
120 |  |  | 300
185 |  |  | 400
300 |  |  | 630
500 |  |  | 800
500 |  |  | 1000
630 |  |  | 1200
630 |  |  | 1600
ab